## Compare
Manufacturer | Web Link | Speed (RPM) | Torque (ft-lbs) | Torque note | Price | Notes | Photo
E. H. Wachs P-2 | Link | 0 to 20 Low & High setting | 500 | variable depending on speed | 8745 | Includes wheel adaptor. ($1,500) Needs a 3500 watt genrator
REED Manufacturing | Link |  | 150 | fixed | 1751 | Needs a wheel adapter & generator
Polard Water | Link | 20 | 250 | adjustable | 2949 | Needs a wheel adapter & generator
Hurco Technology Spin Doctor | Link | 30 | 200 | fixed | 4500 | Needs a wheel adapter ($400)… Battery operated
Wheeler Rex Hand Wheel Adapter | Link | Ohio Power Tools offers this for sale at $369. |  |  |  | OPT Link
w
Warranty:
One year on gear box and controls. Three year
warranty on Milwaukee Power Drive and Lithium
Ion Battery.
Spin Doctor Warranty: One year on gear box and controls. Three year warranty on Milwaukee Power Drive and Lithium Ion Battery.

## HH200 Specs
Will the HH200 do the job?
Specs | Max Torque (ft-lbs) | 200 |  | We need | 75 | ft-lbs
For a fully charged battery:
| Max Speed (rpm) | 30
| Run time range (minutes) | 45 | 60
Assuming we had to open or close the gate 30 inches:
|  | Open/close inches | 30
|  | Turns/in | 17
|  | Resulting no. turns | 510
| Power unit speed (rpm) | 30 | 24 | 18 | 12
| Resulting Battery run time (min) | 17 | 21.25 | 28.3333 | 42.5
All are acceptable

## Drill specs
Milwaukee 0721-21 28V Cordless M28 Lithium-Ion 1/2 in. Right Angle Drill
Specifications
Series: | M28
Cordless: | Yes
Length: | 18.5 in.
Weight: | 10.9 lbs.
Batteries Included: | 1
Battery Amp Hours: | 3 Ah
Battery Type: | Li-Ion
Chuck Size: | 1/2 in.
Chuck Type: | Keyed
Handle Style: | D-Handle Grip
Max. Capacity - Steel (Twist Bit): | 1/2 in.
Max. Capacity - Wood (Auger): | 2-9/16 in.
Power Type: | Electric
RPM: | 0 - 400 / 0 - 1,000
Torque: | 1,081 in-lbs. | 90.0833 | Ft-lbs
Voltage: | 28V
Limited Warrenty | 5 year
Battery Warrenty | 2 year
Web Link